


CAMBRIDGE WATER, SEWER, AND STORMWATER COMMITTEE
AMUNDSON COMMUNITY CENTER`
200 SPRING STREET - COMMUNITY ROOM
JUNE 17, 2025
	Approved 7-15-25	6:30PM
MINUTES      

1. Call to Order/Roll Call: Hollenbeck called the meeting to order at 6:30pm. Members present: Steve Struss, Ted Kumbier, and Paula Hollenbeck. Members absent: Sarah Schulz, and Mat Hughson. Others present: Matt Castillo, and Chase Przybylski from MSA Engineering. Village Staff: Water Operator Derek Schroedl, and Utility Clerk Vicki Redford.

2. Proof of Posting: Agendas were posted in the upper and lower levels of the Amundson Community Center, Badger Bank, Cambridge Post Office, and the Village Website.

Hollenbeck made a motion to move Public Comment to the top of the agenda. Struss seconded. Motion carried. 
Hollenbeck made a motion to move 6a.to be discussed next. Struss seconded. Motion carried
3. Approval of consent agenda
a. Meeting Minutes from 05-20-2025 
Struss made a motion to accept the consent agenda. Hollenbeck seconded the motion. Kumbier abstained because he was absent from the May meeting. Motion carried. 
  
4. Approval of Bills
Kumbier made a motion to accept the bills in the amount of $306,125.67 Hollenbeck seconded the motion. Motion carried on a 3-0 roll call vote.

Struss questioned a bill for OMNI Meters. Schroedl told the Committee that bill was to replace the inside of two different meters. One for At Home Again, and one for the School District. 

5. Reports
a. Utility Clerk: I have been busy with my regular office duties. Doing a lot of meter change outs, and new accounts as well as move in/move out paperwork. We have been working hard to get the office organized.

b. Staff Report: Schroedl told the Committee that Intercon is replacing a gas main. They are pulling manholes looking for laterals. The manhole on north street had to be replaced. Fox & Son did the work and should be about $7500.00. Intercon is basically televising our sewers. They are able to map laterals. Schroedl will be adding this information to our GIS system.
Schroedl said he would like to put a large amount of money towards sewer lining. Hollenbeck asked Schroedl to bring what he thinks needs to be replaced to the July meeting. When we have a completed budget, we will know how much can be spent on lining sewers. Derek will also be abandoning the sewer line by the old Fur Company.
Schroedl has been training Cody Garcia on how to install meters and MXU’s and helping him to work in the water department as well as public works. 
Struss and Hollenbeck noticed that chlorine has been high on the testing sheets. Schroedl said chlorine has been leaking from well #3 and causing the numbers to be higher. He is replacing the fittings to help with the chlorine leakage at well #3. Committee members asked for the heading by manganese on the testing sheets to be changed to N/A.

c. COWC Report: Struss said there was a hit at the plant a month ago. They are not sure where it came from. They had a meeting with the Clearinghouse people working on the phosphorus trading with the DNR. DNR said they will not allow adaptive management. They will not approve of constructed wetland. There is a farm in our water shed, we will wait to see what points the DNR will give for that. 
6. Old Business: Discussion and Possible Action Regarding

a. Well #3 Final Payment and Closeout: - MSA
Chase Przybylski from MSA said the contract has been fulfilled. It is his recommendation to pay the final bill to Mid-City Corp. for $240,4013.91. The warranty is for one year. If there is any issue in that year’s time, the one-year warranty starts over. There was a new backwash pump replaced. Schroedl thinks it is time to close out the project. However, there was an alignment issue. Przybylski said alignment issues are quite common with wells. There is a vibration in the well. Schroedl had it evaluated today. Hollenbeck said we need to fix the alignment issue. Przybylski said Mid-City has tried three things to take care of the problem. They shimmed it. They also raised it up by eighty feet. The final option would be to replace the pump with a submersible pump. Przybylski recommends having an alignment test done at the time the pump is replaced. The Committee agreed that when the current pump wares out, we will replace it with a submersible pump. Hollenbeck suggested setting aside money for this purchase in the future.

Struss made a motion that we accept the recommendation from MSA and make the final payment to Mid-City of $240,403.91 and close-out the Well #3 project. Kumbier seconded the motion. Motion carried on a 3-0 roll call vote. 

Schroedl also said that Mid-City has offered to reseed the grass at Well #3. 
 
b. Water Tower Cleaning: Schroedl asked the contractor if the quote for the tower cleaning was still good. He said yes, the quote is still good. Hollenbeck said that after our budget is done this will be put on a future agenda. 
 
7. New Business: Discussion and Possible Action Regarding

a. Pulliam Large Water Usage at 706 Townsend St. - Utility Clerk
Zach Pulliam was not able to attend the meeting. He provided a letter that was included in the packet. The extra water that was used was a hose that was left on in the back yard.
Struss made a motion to give Mr. Pulliam a sewer credit for the additional 4,000 gallons of water used above his average. Hollenbeck seconded the motion. A full sewer credit was given without
Using the typical sewer credit formula because they know the water did not go down the sewer system. 

b. Bulk Water Dispensing Station: - Water Operator
                  Schroedl said the solar project is using 7-8 loads of water a day. Schroedl has talked
                  to several companies that said they would use a Bulk Fill Station a lot if we had one
                  here in the Village. There was discussion about whether the solar company would  
                  contribute to the cost of the station, and where it would be placed. The Committee 
                  would like Administrator Peterson, and Water Operator Schroedl to contact the solar
                  company about assistance with the cost of the Water Filling Station.
  
8. Public Comment:
Matt Castillo from MSA asked if the Dancing Goat Sampling Plan was going ok. Committee Member Struss said everything has been going well with the Dancing Goat Distillery. Struss said he thinks the occasional issues at the COWC may be coming from someone else. 
Castillo said that Rockdale is moving along with the Regionalization project. He talked to General Engineering, and they bid the project. Castillo said he recommends they not award the bid until we have an agreement with Rockdale. There was a discussion about if Rockdale is being billed for the work on the project. They are being billed for our engineers and attorneys. The Committee discussed how Rockdale will be charged for the sewer service if it moves forward. There are things that will have to be worked out as the project is discussed in the future.  

Mat Hughson called into the meeting at 7:25pm on Hollenbeck’s phone. 

9. Questions, Referrals to Staff or Future Agenda Items:
1. Regionalization
2. Update on Budget
3. Sewer Lining/Abandon sewer line by old fur company
4. Bulk Water Station

10. Adjournment: Kumbier made a motion to adjourn the meeting. Struss seconded the motion. Hollenbeck adjourned the meeting at 7:48pm.



Vicki Redford - Utility Clerk


a) Persons needing special accommodations should call 608-423-3712 at least 24 hours prior to the meeting.
b) More specific information about agenda items may be obtained by calling 608- 423-3712.
c) Final Agendas are typically posted by 4 PM on the Friday preceding the regular meeting at the Amundson Community Center, Cambridge Post Office, Badger Bank and Village of Cambridge Web site at 



